## HFOct1
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | BatchDspl |  | Matt Mummert
Hot Fix CR# | L00129111 | Hot Fix Status: | Released-Unverified
Summary: | (Diagnostic Hotfix) SR 24910175 -:- [Genentech] Batch Display not loading properly - shows mixed info of 2 batches
Actual Result: | Back to the beginning, what they saw actually involved a Ready batch. See below. The phase/parm is showing batch running on T446 whereas sfc is showing batch to be started (grey with no equipment yet allocated) and run on T434. -Matt On 9/13/2013 6:55 AM, Stella Lee wrote: Yesterday, a couple of technicians noticed that the batch display was not loading correctly. The CLB was loading fine, but the section for the M instructions were displaying another recipe. I asked the techs the replicate the issue. They did this on 091213 ~ 0100. They scheduled 434Harv line CIP, but the top and middle section of the batch display loaded T446. The unit procedures and phases on the bottom section loaded properly, displaying the 2KHarv recipe. After waiting for a minute, nothing changed. They closed down the batch display and selected the the 2K harv recipe again and it did the same thing. After the 3rd attempt the 2Kharv recipe loaded properly. Speaking to another technician from days, he observed this issue as well. Stella
Expected Result: | Info about selected batch only.

## HFOct2
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Extensibility 3.6
Component | SuiteLinkDDEProxy |  | Paul McGuire
Hot Fix CR# | L00129089 | Hot Fix Status: | Released-Unverified
Summary: | SR 37112888 & SR 103128979 - When a remote data source node time syncs, timestamp out of sequence warnings occur for every item being polled
Actual Result: | Related to investigation L00125102 Customer uses DDESL to read from remote node. That remote node has a forward time drift. When time sync occurs hourly and the remote node time is shifted backwards, a Warning is logged for every item being polled. (Imagine if a customer was pollling 20000 items, they would get 20000 warnings.) Message is similar to this: Log Flag: Warning ¦ Component: DDESuitelinkClient ¦ Message: Item 16777297: 'BrewKettle200.temperature.pv' has a timestamp out of sequence: previous T-Q 2/6/2013 18:40:55.93-c0, current T-Q 2/6/2013 18:40:52.683-c0. Time synchronization can be out of spec, please verify galaxy time synchronization to avoid data loss.
Expected Result: | This warning mechanism has limited or no value for many customers, yet creates a potential for large-scale log flooding. It seems this was implemented by L00120440. The only way to supress the warning is to disable all DDESuitelinkClient component Warning messages, which is not a very good workaround. Suggested improvements: - Move this warning to its own dedicated log flag so it could be disabled if undesired. It could then be enabled for troubelshooting or in cases where the customer wants to see all these warnings. - Perhaps it would be better to log one warning per topic, instead of one warning per item? If you have timetamp issues, it is very likely that many items will be impacted. Maybe there are even two new log flags? (Topic time problems or item detail time problems?) - Is this even warning worthy? Perhaps info is sufficient. Not sure on this one. - Maybe a registry setting to set a tolerance would be good? For exmaple if the time if off by <100ms, don't bother logging the message? If this is a setting, it could be tweaked to reduce log noise for customers with the log flag enabled and ensure they only log serious time shift issues.

## HFOct3
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InBatch InBatch 10.0
Component | IBMX |  | Don Tunnell
Hot Fix CR# | L00129061 | Hot Fix Status: | Released-Unverified
Summary: | (HF Rollup for 10.0) Invensys service custoerm Cytec is seee issue with IBMX throwing messages related to "Timeout on START UPDATE tag request (waiting for good quality) [UDTP1I1.DOSIMAN.KGS.MATID] - returning bad quality. Current quality [0x40].
Actual Result: | SR 15712647 - IBMX throwing messages related to "Timeout on START UPDATE tag request (waiting for good quality) [UDTP1I1.DOSIMAN.KGS.MATID] - returning bad quality. Current quality [0x40]. This behavior is noticed only for string tags. InBatch Tags are linked to AppObject Attributes and the customer is using IBMX to communicate between InBatch and AppServer. The quality of the app object attributes is good in ObjectViewer, however the log messages show a quality of 40. This issue needs to be investigated. I have setup the customer application at some point in time and we did not see the behavior customer reporting. However, I am testing only a single phase using customer Config_a and their galaxy. Attached shows the log files with tracing turned on for IBMX, customer using "Advise All" and also we have dump files for BatchMngr and also IBMX. If customer uses suitelink and link the same tags to IBCli there are no issues. Customer using InBatch 2012 (9.6) with System Platform 2012. I am using InBatch Beta (2012 R2) and System Platform 2012 R2. I like you guys to atleast look at the dump files and see why InBatch shows a a quality of 40. Unfortunately, customer doesn't have internet access and cannot remote to their machines. I have their config_a and confirmed that string tags are directly pointing to appobject attributes and they are not linked to PLC. If developer wants to see the config_a and galaxy, I will provide the access to my test system here in the lab.
Expected Result: | See actual results

## HFOct4
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | ArchestrA Graphics |  | Luca Bruni
Hot Fix CR# | L00128936 | Hot Fix Status: | Released-Unverified
Summary: | [XREF SR103129629 - Wonderware France (LFB)] - Non standard behavior on Archestra Graphics Halo
Actual Result: | In some cases the alo around an ArchestrA graphic object is still displayed even if the mouse cursor is no more in it.
Expected Result: | Halo should be drawn only when the mouse cursor is on the ArchestrA graphic object.

## HFOct5
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | InTouch |  | Michael Ang
Hot Fix CR# | L00129052 | Hot Fix Status: | Released-Unverified
Summary: | [Azbil] SR# 41810110 - Issues regarding halo and animation link
Actual Result: | When 2 animation with with DialogValueEntry is place near to each other, clicking on the halo of 1 animation will trigger the dialog box of the other animation
Expected Result: | click on the halo should activate the action for that particular animation is not the one near to it

## HFOct6
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5 Patch01
Component | Alarms |  | Mirko Canel
Hot Fix CR# | L00129068 | Hot Fix Status: | Released-Unverified
Summary: | [Genentech] OLD Alarm transitions are changing state upon platform restart and reinserted in alarmdb
Actual Result: | POSSIBLE ISSUE INTRODUCED WITH CHANGES DONE FOR : L00123877 After platform restart we found old alarms re inserted in the alarm database but with Status changed. Attached Email chain with the customer with all the details. 1574411 and 1574410 are duplicates of 1573860 and 1573859 but have been reinserted with a Different STATUS. AlarmDetailId AlarmId AlarmTransition AlarmState AlarmType Priority OutstandingAcks Limit LimitString ValueString TransitionTime TransitionTimeFracSec 1574411 835218 ACK ACK_RTN DSC 6 0 NULL true false 2013-10-03 21:16:39.327 3277 1574410 835218 RTN UNACK_RTN DSC 6 1 NULL true false 2013-10-03 21:16:46.483 4839 1573860 835218 RTN ACK_RTN DSC 6 0 NULL true false 2013-10-03 21:16:46.483 4839 1573859 835218 ACK ACK_ALM DSC 6 0 NULL true true 2013-10-03 21:16:39.327 3277 1573786 835218 ALM UNACK_ALM DSC 6 1 NULL true true 2013-10-03 19:35:48.103 1034
Expected Result: | Fix

## HFOct7
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Extensibility 3.6
Component | OPC Proxy |  | Paul McGuire
Hot Fix CR# | L00129116 | Hot Fix Status: | Released-Unverified
Summary: | [SR 103128979/Marathon] Successive values reported to OPC client with same timestamp are benign, but generate a flood of warning messages in the SMC log.
Actual Result: | Many errors of the form: Item 9090: 'A126G50.STATUS' has a timestamp out of sequence: previous T-Q 7/12/2013 10:5:6.343-c0, current T-Q 7/12/2013 10:5:6.343-c0. Time synchronization can be out of spec, please verify galaxy time synchronization to avoid data loss. For multiple tags over and over again on 2 AOS node. Systems are Time Synch'd to the domain. Note that the 2 timestamps are equal, not out of sequence.
Expected Result: | No messages if successive values have equal timestamps.

## HFOct8
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | Input Primitive |  | Manal Hany
Hot Fix CR# | L00129092 | Hot Fix Status: | Released-Unverified
Summary: | SR 103129816 HF L125088 and L127921 not included in P01 from ASP3.6 - the tag.input.value and tag value are not the same when you have "Generate event upon change" for this attribute
Actual Result: | In objectviewer, when an object's "Analog_001.Input.Value" and "Analog_001" are both added into the watchlist and you remove "Analog_001.Input.Value", "Analog_001" stops updating. This occurs when "Generate event upon change is enabled" I’ve found a workaround, but customer did not accept it, they requesting a HotFix instead. In galaxy IDE, in the top menu bar go to Galaxy -> Configure -> Communications Management… In the ‘Configure Communications Management’ pop-up window there’s a checkbox ‘Enable advanced communications management’. Uncheck it. After this you have to stop and restart the platform. It should work.
Expected Result: | After removing "Analog_001.Input.Value", "Analog_001" keeps updating.

## HFOct9
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | WindowMaker |  | Michael Ang
Hot Fix CR# | L00129051 | Hot Fix Status: | Released-Unverified
Summary: | [Azbil]SR# 41810181 - Unexpected window location change during development
Actual Result: | When performing certain sequence of event in the Window Maker, the windows X,Y location will change without the user maunally changin it.
Expected Result: | The X,Y location should not change without user manually changing them

## HFOct10
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6
Component | GRLoadServer |  | Peter Von tluck
Hot Fix CR# | L00128575 | Hot Fix Status: | Released-Unverified
Summary: | SR45110229: Dillinger Huette (Premium): Galaxy load (csv) of only few instances (changed parameters) takes several hours.
Actual Result: | Dillinger Huette did migration of IAS 3.1 sp.3 p1 to 2012 R2. Actually the database (SQL Server 2012) has about more than 8 GByte. They do changes on instances by importing parameters via csv Galaxy load. In case they did the import for only 32 instance which had been changed on 2 attributes only this took more than 2 h. We were able to reproduce that behavior. The most time consuptive sp was internal_mark_view_app_for_redeploy, which took about 5 min at one time. Additionally the databse was growing during import from 14 to 27 gByte. The biggest table was visual_element_reference table: 30 MIO rows, 13 GByte internalk reserved.
Expected Result: | why does it take so long to import changes for only few instances?

## HFOct11
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | ArchestrA Graphics |  | Spark Hong
Hot Fix CR# | L00128875 | Hot Fix Status: | Released-Verified
Summary: | SR 103129702 - Can't substitute strings of embeded symbol in Window Maker if the strings of texts contain double-byte characters.
Actual Result: | Can't substitute strings of embeded symbol which contain double-byte characters in Window Maker. The same issue doesn't happen on InTouch 10.5 ad all previous version.
Expected Result: | The strings should all be substituted correctly.

## HFOct12
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | WW MES 4.5
Component | Middleware |  | Andrea Sartori
Hot Fix CR# | L00129099 | Hot Fix Status: | Released-Unverified
Summary: | [Customer:Nestle][SR:34211452] Nestle needs to use SQLNCLI provider for the connect string of the middleware, but some problems show up already during MES client login. We need to know the feasibility to adapt for using this provider instead SQLOLEDB.
Actual Result: | Nestle uses high availability mirroring in their latest version of the MES library. Using SQLOLEDB provider for the connect string will not allow to connect in case the database is currently active on the redundant server, as the "Failover Partner" attribute is ignored by the provider (outcome of a MS investigation on the connection issue). Microsoft suggested to switch to SQLNCLI provider but, after a quick test replacing provider name, it appears that there are some compatibility issues: -middleware connected properly -starting MES client with no users defined (so no logon) it showed up with no apparent errors -starting MES client with admin user defined raised errors already at the moment of logging in
Expected Result: | We would need to check if the software can work (or if it is feasible to adapt it) with SQLNCLI provider.

## HFOct13
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | WWInfoServer 4.0 SP1
Component | Portal |  | Peter Von tluck
Hot Fix CR# | L00128682 | Hot Fix Status: | Released-Unverified
Summary: | SR45110269: Porsche Premium account. WIS 4.0 sp. 1 should be supported with InternetExplorer 10
Actual Result: | WIS 4.0 sp. 1 is not supported with IE 10
Expected Result: | WIS 4.0 sp. 1 is has to be supported with IE 10

## HFOct14
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | WW MES 4.5
Component | Reports - AA |  | Jim Godfrey
Hot Fix CR# | L00129022 | Hot Fix Status: | Released-Verified
Summary: | Cannot view charts in the Quality Characteristic Detail Report (SPC)
Actual Result: | When the report is Executed, there is an error where the charts should be; "Error: Subreport could not be shown."
Expected Result: | The quinn curtis charts should be shown without error

## HFOct15
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | Application Category |  | Luca Santinello
Hot Fix CR# | L00129017 | Hot Fix Status: | Released-Unverified
Summary: | SR 103129747: Customer requires HF for CR L00124147 porting to 3.6 patch 1. "Enable state label" for Discrete Field Attribute does not work for OPR events.
Actual Result: | "Enable state label" for Discrete Field Attribute does not work for OPR events
Expected Result: | it should work good

## HFOct16
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | View |  | Jozef Krehel
Hot Fix CR# | L00129058 | Hot Fix Status: | Released-Unverified
Summary: | SR 103129187, 42010090, 103129638 - View disappears after the main window shows for a few seconds [Porting HF for French version]
Actual Result: | City of Snohomish. Deployed ViewApp has been running for months. Monday morning Sept 24 at 7:11 AM it was not able to be run anymore. View disappears after the main window shows for a few seconds. Tried various things including rebuilding the operating system, but the problem remains. The same ViewApp can be deployed to the GR node and runs fine. Note that the View node is Windows 7 SP1 64 bit and the GR node is Windows 2008 R2. The other strange thing is the app ran on the View node once after rebuilding the operating system, but was not able to run in repeated attempts after that. Various files are attached to this CR. The most important are: ViewCrashLogFile.JPG - Screen shot of Log File showing error message "Failed to reconnect to data source" from InTouchProxy. Notice that the SessionID is not the same session as View. "20120924 Logs InTouch wont start.zip" (stored at \\devsql01\CQ-Attachement\L00123000 ) contains: DWVIEW1 LogExport9242012.aaLGX - Log File view__PID__4760__Date__09_24_2012__Time_07_11_04AM__9__Second_Chance_Exception_C0000008.dmp - first dump file at 7:11 AM view__PID__3084__Date__09_24_2012__Time_07_52_26AM__165__Second_Chance_Exception_C0000008.dmp - second dump file at 7:52 AM Prerana Kulkarni has already done a dump file analysis. See attached dump file analysis attachment. The main comment is: From what I see in Windbg: View places a call to Microsoft API: GetUsedGDIHandlesCount and after that there is a crash.
Expected Result: | View not to crash.

## HFOct17
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | AAWebGraphics 4.5
Component | aaWXE |  | Spark Hong
Hot Fix CR# | L00129077 | Hot Fix Status: | Released-Unverified
Summary: | SR 46110225 - the animation in published window is not working correctly as in InTouch Viewer, after clicking the window link twice, it works correctly. Port the HF-L00128876 from 4.1 to 4.5.
Actual Result: | The animation is not working correctly in WIS as same as in InTouch Viewer, after click the link of the window in navigation panel again, it is working! Note: the same behviour observed in another customer's site with WIS 4.5. I'm looking to see if they are the same root cause.
Expected Result: | The animiation is WIS window should be working as the same behaviour as InTouch Viewer.

## HFOct18
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | WW MES 4.0 SP 2
Component | Database Scripts |  | Darryl McKenna
Hot Fix CR# | L00127322 | Hot Fix Status: | Released-Unverified
Summary: | Wonderware North customer JMC steel has an issue with TPM_STAT from item_prod does not alway calculate correctly related to the byProduct. Related CR L00121705, SR 103128887 and SR 103128888,
Actual Result: | TPM_STAT is calculated incorrectly when call aaMES.Prod.aaJobExec.AddProdPostExec for a ByProduct where the shift is not the current shift.
Expected Result: | TPM_STAT should be correct, with the quantities of the byProduct ignored for both the current and historical shifts.

## HFOct19
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | WW MES 4.5
Component | Reports - AA |  | Jim Godfrey
Hot Fix CR# | L00129022 | Hot Fix Status: | Released-Unverified
Summary: | Cannot view charts in the Quality Characteristic Detail Report (SPC)
Actual Result: | When the report is Executed, there is an error where the charts should be; "Error: Subreport could not be shown."
Expected Result: | The quinn curtis charts should be shown without error

## HFOct20
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | Retrieval Service |  | Tomas Balla
Hot Fix CR# | L00128501 | Hot Fix Status: | Released-Verified
Summary: | SR# 49010006 - Workbook doesn't display null es where the timestamp is in future
Actual Result: | Client has many Historian Client Workbooks using functions like Maximum, Minimum, etc for Production Reporting. They use running totals for the day. When a user opens the workbook, it reflects everything for the day. For the dates/times taht are in future the workbook displays the last known value. When using Historian 10 SP1 and Historian 10.1 (System Platform 2012), these values were displayed as null values. Client upgraded to System Platform 2012 R2 (Historian 11 and Historian Client 10.1). Now the values show the last known value.
Expected Result: | For the future timestamps workbook displays NULL values.

## HFOct21
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InBatch InBatch 10.0
Component | OCXBatch |  | Srinivas Mariyala
Hot Fix CR# | L00128999 | Hot Fix Status: | Released-Unverified
Summary: | SR 103129399 - When a view application is converted from older version to 10.0, during compilation of windows, "Not connected to BatchServer!" message comes up four times.
Actual Result: | SR 103129399 - When a view application is converted from older version to 10.0, during compilation of windows, "Not connected to BatchServer!" or "missing or improperly configured batchguiconfigctrl" message comes up four times. After compilinng windows, customer goes in and makes a simple change to a window, and it compiles all windows and when he goes to view, it does same thing again. Originally, it was understood that, may be scripts getting fired before controls not even initialized and can't reproduce the issue with simple test application. Actually customer narrowed down the problem to tags that are linked to list control. When the tags unlinked from these list controls, then problem goes away. Again with a simple test application, the issue is not reproducible. I will run the test with a older version of InTouch application and update the CR. With cusotmer application, this is easily reproducible, see the steps. Need to be investigated and see why the application is complaining about missing controls. This behavior was not there with older versions of InBatch.
Expected Result: | See actual results.

## HFOct22
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.1 SP2 Patch01
Component | Attribute Browser |  | David Ujifusa
Hot Fix CR# | L00129001 | Hot Fix Status: | Released-Verified
Summary: | [XREF CRL103122826] [Customer:Astor sp z.o.o.] [Symptom: Filtering the object by contained name in ArchestrA Graphic Editor when selecting alternate instance even if there is an object with the name that contains the filter will return a blank window]
Actual Result: | If the customer perform a filter after choosing 'Select Alternate instance' in the ArchestrA graphics editor for a text that is contained into all the instances already shown up, instead of showing up the same result, it returns a blank window with no instances shown.
Expected Result: | All the instances that contains the text selected in the filer must be shown. This behavior impacts on selecting the correct instance in a big Galaxy.

## HFOct23
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | LMX |  | Jozef Krehel
Hot Fix CR# | L00128736 | Hot Fix Status: | Released-Verified
Summary: | SR 42010087 - Thames Water - Errors in SMC :OnNamespaceItemResolved item id returned from service [28612] is different from asked
Actual Result: | The hotfix L00128448 has improved matters - FSGateway no longer hangs when polling for data. However, instead, around 25% of the time the customer gets the following warnings in SMC: OnNamespaceItemResolved item id returned from service [28612] is different from asked for [28611]
Expected Result: | Communication working properly and no warning messages in SMC.

## HFOct24
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | InTouch |  | vladimir veselenyi
Hot Fix CR# | L00128748 | Hot Fix Status: | Released-Verified
Summary: | SR#103129522 PostLogon Dialog box can be hidden behind popups , seems like similar to L00046397, is not reproducible on 3.6 P01
Actual Result: | PostLogon Dialog box can be hidden behind InTouch popup windows what causes application to freeze , seems like similar to L00046397, seems that patch 01 for 3.6 fixed this issue so they want to port the fix to 3.1 SP3 P01
Expected Result: | The dialog box should be modal to all InTouch windows

## HFOct25
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6
Component | Input Primitive |  | Tomas Balla
Hot Fix CR# | L00127921 | Hot Fix Status: | Released-Verified
Summary: | SR 103129029 - the tag.input.value and tag value are not the same when you have "Generate event upon change" for this attribute
Actual Result: | In objectviewer, when an object's "Analog_001.Input.Value" and "Analog_001" are both added into the watchlist and you remove "Analog_001.Input.Value", "Analog_001" stops updating. This occurs when "Generate event upon change is enabled" I’ve found a workaround, but customer did not accept it, they requesting a HotFix instead. In galaxy IDE, in the top menu bar go to Galaxy -> Configure -> Communications Management… In the ‘Configure Communications Management’ pop-up window there’s a checkbox ‘Enable advanced communications management’. Uncheck it. After this you have to stop and restart the platform. It should work.
Expected Result: | After removing "Analog_001.Input.Value", "Analog_001" keeps updating.

## HFOct26
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0
Component | N/A |  | Tomas Balla
Hot Fix CR# | L00128362 | Hot Fix Status: | Released-Verified
Summary: | SR# 103129194 - After a restart of the Historian or a redeploy of the Engine, former tags reappear
Actual Result: | This is a clone from CR# L00128053. At first it seemed that the HF L00127278 did solve the problem. In some cases though, the deleted tags still reappear. Original description: When you delete existing objects with historized tags from an engine and you remove these tags from the Historian MDAS configuration, you will see again these tags from the Historian after a reboot of the Historian or after a redeploy of the engine. This issue was not present with older versions of System Platforms
Expected Result: | Tags do not reappear.

## HFOct27
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | AAWebGraphics 4.0 SP1
Component | aaWXE |  | Spark Hong
Hot Fix CR# | L00128876 | Hot Fix Status: | Released-Verified
Summary: | SR 103128229/46110225 - the animation in published window is not working correctly as in InTouch Viewer, after clicking the window link twice, it works correctly.
Actual Result: | The animation is not working correctly in WIS as same as in InTouch Viewer, after click the link of the window in navigation panel again, it is working! Note: the same behviour observed in another customer's site with WIS 4.5. I'm looking to see if they are the same root cause.
Expected Result: | The animiation is WIS window should be working as the same behaviour as InTouch Viewer.

## HFOct28
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | WindowViewer |  | Alex Chia
Hot Fix CR# | L00128803 | Hot Fix Status: | Released-Verified
Summary: | xRef hotfix L00128532. Require same hotfix, for InTouch Japanese xRef SR 48110021 view.exe crash after doing analog input, and then close window. Replicated in IT 10.5 P01. Customer is HIRANO TECSEED CO., Ltd (35305)
Actual Result: | In a window with a historical trend chart, after filling in 3 analog input text boxes, and then pressing a button to close the window. Hd.exe crashes
Expected Result: | These actions should not cause hd.exe to crash

## HFOct29
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5 Patch01
Component | LMX |  | Alex Chia
Hot Fix CR# | L00128616 | Hot Fix Status: | Released-Verified
Summary: | xRef SR 42410249 When only Backup AppEngine is deployed, Advanced Communication Mgmt enabled, I/O Data is not subscribed when only scripts uses I/O data, without Client (IT or ObjViewer) viewing point. GlobalCyberSoft, SiteID 146922, Cust 1st 109237
Actual Result: | When only Backup AppEngine is deployed and Advanced Communication Mgmt enabled I/O extended attribute data is not refreshed when only scripts uses attribute for calculation This is when, there is no client viewing data, InTouch or Object Viewer Obj1.iEquipmentStatus is I/O Extended Obj1.iEquipmentStatus2 not I/O Extended, defaults to 0 Obj1 has a script that calculates the sum of Obj1.iEquipmentStatus and Obj1.iEquipmentStatus2 into Obj1.iCalculatedStatus
Expected Result: | I/O Extended data should be refreshed when even if there is no client when there is script using the attribute. Obj1.iEquipmentStatus is I/O Extended Obj1.iEquipmentStatus2 not I/O Extended, defaults to 0 Obj1 has a script that calculates the sum of Obj1.iEquipmentStatus and Obj1.iEquipmentStatus2 into Obj1.iCalculatedStatus Calculation of attributes should be functioning well even if Obj1.iEquipmentStatus is not visible in ObjectViewer or InTouch.

## HFOct30
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.1 SP2 Patch01
Component | Attribute Browser |  | David Ujifusa
Hot Fix CR# | L00129001 | Hot Fix Status: | Released-Unverified
Summary: | [XREF CRL103122826] [Customer:Astor sp z.o.o.] [Symptom: Filtering the object by contained name in ArchestrA Graphic Editor when selecting alternate instance even if there is an object with the name that contains the filter will return a blank window]
Actual Result: | If the customer perform a filter after choosing 'Select Alternate instance' in the ArchestrA graphics editor for a text that is contained into all the instances already shown up, instead of showing up the same result, it returns a blank window with no instances shown.
Expected Result: | All the instances that contains the text selected in the filer must be shown. This behavior impacts on selecting the correct instance in a big Galaxy.

## HFOct31
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | ArchestrA Graphics |  | Spark Hong
Hot Fix CR# | L00128875 | Hot Fix Status: | Released-Unverified
Summary: | SR 103129702 - Can't substitute strings of embeded symbol in Window Maker if the strings of texts contain double-byte characters.
Actual Result: | Can't substitute strings of embeded symbol which contain double-byte characters in Window Maker. The same issue doesn't happen on InTouch 10.5 ad all previous version.
Expected Result: | The strings should all be substituted correctly.

## HFOct32
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | N/A |  | Tomas Balla
Hot Fix CR# | L00129032 | Hot Fix Status: | Released-Unverified
Summary: | SR# 103129346 - Port ths HF from 3.6 to 3.6 P01 - After a restart of the Historian or a redeploy of the Engine, former tags reappear
Actual Result: | This is a clone from CR# L00128053. At first it seemed that the HF L00127278 did solve the problem. In some cases though, the deleted tags still reappear. Original description: When you delete existing objects with historized tags from an engine and you remove these tags from the Historian MDAS configuration, you will see again these tags from the Historian after a reboot of the Historian or after a redeploy of the engine. This issue was not present with older versions of System Platforms
Expected Result: | Tags do not reappear.

## HFOct33
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | Alarm DB Logger |  | Ravi Kandula
Hot Fix CR# | L00129005 | Hot Fix Status: | Released-Unverified
Summary: | SR103121680 - In the historian SQL the alarm type column is char 6, but only 4 char's are displayed in the field. HOtfix requested for 10.6.001
Actual Result: | The customer is using the WWALMDB_logger to collect all alarm information in the system. When opening the alarm detail table in the historian SQL they see that the alarm type column is char 6, but only 4 char's are in the field. This makes the alarms HIOU, STAT or HIAB when they should be HIOUT, STATE or HIABS...
Expected Result: | All Characters (up to 6 which is the limit of the field) should be displayed.

## HFOct34
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.5
Component | DB Load |  | Tomas Balla
Hot Fix CR# | L00128908 | Hot Fix Status: | Released-Unverified
Summary: | SR# 41010031 - tagname.comment and tagname.alarmcomment doesn't change
Actual Result: | changes to tag dictionary by DBLoad is not delivered to client nodes via NAD functionality in InTouch 10.1 SP3 P01. As is always the case with Azbil, it claims that it had been working alright with legacy 7.11 version
Expected Result: | Changes to tags using DBLoad should filter to all the NAD clients

## HFOct35
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | AAWebGraphics 4.0 SP1
Component | aaWXE |  | Spark Hong
Hot Fix CR# | L00128876 | Hot Fix Status: | Released-Unverified
Summary: | SR 103128229/46110225 - the animation in published window is not working correctly as in InTouch Viewer, after clicking the window link twice, it works correctly.
Actual Result: | The animation is not working correctly in WIS as same as in InTouch Viewer, after click the link of the window in navigation panel again, it is working! Note: the same behviour observed in another customer's site with WIS 4.5. I'm looking to see if they are the same root cause.
Expected Result: | The animiation is WIS window should be working as the same behaviour as InTouch Viewer.

## HFOct36
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | FS Gateway 3.0
Component | Runtime |  | Dan Scott
Hot Fix CR# | L00128439 | Hot Fix Status: | Released-Unverified
Summary: | SR 37113181 - If item activation occurs rapidly, items improperly go to bad quality. Data can become stale or null value with good quality.
Actual Result: | Customer is using FSGateway 3.0 + HF L00127971 (Build 355.226.9.5) Customer is using App Server to FSGateway to Opto OPC Server If non-changing items are rapidly deactivated and reactivated on the Suitelink interface, FSGateway sends only the activate command to the OPC server. Since the OPC server knows that the items are already active, it does not reply with a new OnDataChange update. After nearly 2 minutes, FSGateway logs an error and marks the items as bad quality, since it was waiting for that new data information. The quality will not change until the value changes in the OPC server and a new OnDataChange is received. Error: Initial update from OPC server after activation/creation of item 'Dpoint;State;A_66_15_00_BHCIPRP' in topic 'BH1_DIO' never occurred, injecting bad quality 18h
Expected Result: | FSGateway should properly handle quick deactivation/activation activities

## HFOct37
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Intelligence 1.5 SP1
Component | Runtime |  | Chris Boutcher
Hot Fix CR# | L00128553 | Hot Fix Status: | Released-Unverified
Summary: | SR103129335 - Intelligence - 1.5 SP1 : Timeout on Measure updates
Actual Result: | <<Log #103129335 - Ernst VanWyk, WW-SouthAfrica (on behalf of Transnet Freight Rail)>> Customer is encountering problems deploying some very large measures. Deploying a measure will start the backfill – after about 20 to 40 million records (20 to 40 minutes) the logfile shows a timeout for the connection and stops. o The timeout appears not to be for a query, but for the actual connection. o The timeout appears to be hard-coded for 2 minutes; customer has tried modifying settings in the "IntelligenceDataAdapterService.exe.config" file, but no effect. o Once this timeout exception is thrown, the system never retries: It stops the entire backfill right there and then.
Expected Result: | Investigation CR #L000128405 for this case found the measure ETL is not using the configurable QueryTimeout parameter (from the EMIiRuntimeConfigurator.xml file) and the SQL Command issued during ETL is configured with a timeout that is using the default of 120 seconds. In the customer's case, this is not sufficient since they are experiencing a command timeout during the second stage of ETL processing. It is recommended that the measure ETL be modified to use the QueryTimeout parameter or something else that can be configured manually beyond the hard-coded default 120sec.

## HFOct38
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0
Component | N/A |  | Tomas Balla
Hot Fix CR# | L00128362 | Hot Fix Status: | Released-Unverified
Summary: | SR# 103129194 - After a restart of the Historian or a redeploy of the Engine, former tags reappear
Actual Result: | This is a clone from CR# L00128053. At first it seemed that the HF L00127278 did solve the problem. In some cases though, the deleted tags still reappear. Original description: When you delete existing objects with historized tags from an engine and you remove these tags from the Historian MDAS configuration, you will see again these tags from the Historian after a reboot of the Historian or after a redeploy of the engine. This issue was not present with older versions of System Platforms
Expected Result: | Tags do not reappear.

## HFOct39
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 10.0 SP1
Component | Storage |  | Hongjoe Yang
Hot Fix CR# | L00128972 | Hot Fix Status: | Released-Unverified
Summary: | SR :48710002 Replication tag’s average calculation(hourly) has problem when it combine with Remote-IDAS. We found that the calculation becomes wrong between AM 12:00:00 and AM 1:00:00.
Actual Result: | normal average data Average value is in the range of 0~65535. ex) Min:3332 Max:29322 Average:16327.97
Expected Result: | Abnormal average data. ex) Min:37194 Max:38494 Average:19463364673.... StartDateTime:2013-05-16 PM 11:00:00 After calcuated date corrupt, it impact following hour average data also.

## HFOct40
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch InTouch 10.6
Component | WindowViewer |  | Jozef Krehel
Hot Fix CR# | L00127198 | Hot Fix Status: | Released-Verified
Summary: | SR 45510346/45610225/17114377 : When using the function EnableDisableKeys() to disable ALT it also disables CTRL key.
Actual Result: | When using the function EnableDisableKeys() to disable ALT it also disables CTRL key.
Expected Result: | Disabling Alt Key should not disable the CTRL key

## HFOct41
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0
Component | HistorianSDK |  | Vinay Kamath
Hot Fix CR# | L00128740 | Hot Fix Status: | Released-Unverified
Summary: | While querying the tag values continuously using Historian 11 SDK, a memory leak has been observed.
Actual Result: | While querying the tag values continuously for one or two days using Historian 11 SDK , an increase in memory usage (from 240 MB to almost 1 GB) is observed.
Expected Result: | The total memory usage while using Historian 11 SDK should be stable and should be within permissible limits.

## HFOct42
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5 Patch01
Component | LMX |  | Alex Chia
Hot Fix CR# | L00128616 | Hot Fix Status: | Released-Unverified
Summary: | xRef SR 42410249 When only Backup AppEngine is deployed, Advanced Communication Mgmt enabled, I/O Data is not subscribed when only scripts uses I/O data, without Client (IT or ObjViewer) viewing point. GlobalCyberSoft, SiteID 146922, Cust 1st 109237
Actual Result: | When only Backup AppEngine is deployed and Advanced Communication Mgmt enabled I/O extended attribute data is not refreshed when only scripts uses attribute for calculation This is when, there is no client viewing data, InTouch or Object Viewer Obj1.iEquipmentStatus is I/O Extended Obj1.iEquipmentStatus2 not I/O Extended, defaults to 0 Obj1 has a script that calculates the sum of Obj1.iEquipmentStatus and Obj1.iEquipmentStatus2 into Obj1.iCalculatedStatus
Expected Result: | I/O Extended data should be refreshed when even if there is no client when there is script using the attribute. Obj1.iEquipmentStatus is I/O Extended Obj1.iEquipmentStatus2 not I/O Extended, defaults to 0 Obj1 has a script that calculates the sum of Obj1.iEquipmentStatus and Obj1.iEquipmentStatus2 into Obj1.iCalculatedStatus Calculation of attributes should be functioning well even if Obj1.iEquipmentStatus is not visible in ObjectViewer or InTouch.

## HFOct43
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | HCAL |  | Brian Nguyen
Hot Fix CR# | L00128444 | Hot Fix Status: | Released-Unverified
Summary: | SR192110918 - Slow changing UDA (MDAS tag) does not historize after a platform reboot (might be related to CR's L00127564 & L00127486)
Actual Result: | Slow changing or static MDAS tag stops historizing after a platform reboot. ObjectViewer still shows the data value with C0:Good quality and Status Ok, but Historian shows NULL with QD 24 after the reboot of the corresponding AppServer platform. There is no apparent message in the aalogger regarding this issue.
Expected Result: | Slow changing or static MDAS tag should not stop historizing after a platform reboot or networking disruption. We were told this was fixed in Patch01 (CR's #L00127564 & #L00127486), that it would insert a value with QualityDetail=704 "Good value, timestamp overwritten, values out of time sequence" because the reconnected value has an old VTQ timestamp that hasn't changed because the AppServer remained operational. Unfortunately it does not appear to be doing this.

## HFOct44
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | Retrieval Service |  | Tomas Balla
Hot Fix CR# | L00128501 | Hot Fix Status: | Released-Unverified
Summary: | SR# 49010006 - Workbook doesn't display null es where the timestamp is in future
Actual Result: | Client has many Historian Client Workbooks using functions like Maximum, Minimum, etc for Production Reporting. They use running totals for the day. When a user opens the workbook, it reflects everything for the day. For the dates/times taht are in future the workbook displays the last known value. When using Historian 10 SP1 and Historian 10.1 (System Platform 2012), these values were displayed as null values. Client upgraded to System Platform 2012 R2 (Historian 11 and Historian Client 10.1). Now the values show the last known value.
Expected Result: | For the future timestamps workbook displays NULL values.

## HFOct45
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | WindowViewer |  | Alex Chia
Hot Fix CR# | L00128494 | Hot Fix Status: | Released-Unverified
Summary: | xRef SR 41810197 hd.exe crash after doing analog input, and then close window. Replicated in IT 10.1 SP3, and SP3 P01. SP2 not affected. Customer is JFE Engineering Corporation - (124572), has large order coming. xRef CR L00128402 and L00128403.
Actual Result: | In a window with a historical trend chart, after filling in 3 analog input text boxes, and then pressing a button to close the window. Hd.exe crashes
Expected Result: | These actions should not cause hd.exe to crash

## HFOct46
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6
Component | Alarms |  | Luca Bruni
Hot Fix CR# | L00127974 | Hot Fix Status: | Released-Verified
Summary: | SR27811031 - CF Agreement ID: 108768 The customer Giordano\TMB request to connect to the WinPlatform AlarmMgr (Session 0) and Intouch AlarmMgr (Session 1) having them both visible (see attached email).
Actual Result: | The customer TMB\Giordano CF Agreement ID: 108768 is using the Alarm Toolkit and has successfully built a Windows form test application. The test application serves as an Alarm Consumer and an Alarm Provider. He can connect via Intouch and all as well; however, when he takes the same consumer and provider logic and creates a Windows Service – he has the following issues – the service will consume Alarms only after selecting the “Allow service to interact with Desktop” option (this makes sense); however, he cannot connect successfully to get alarms provided by the service based alarm provider. Is a security issue (the service is set to run under the local system account but has also failed when set to the ArchestrA Network account). Is this simply an issue with a desktop application communicating directly with a Windows Service (session issues)? Is there possibly a flag setting that will allow the connection?
Expected Result: | The possibility to connect to the WinPlatform AlarmMgr (Session 0) and Intouch AlarmMgr (Session 1) having them both visible. For resolution see Dev team communications in the attached email.

## HFOct47
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | WindowViewer |  | Alex Chia
Hot Fix CR# | L00128803 | Hot Fix Status: | Released-Unverified
Summary: | xRef hotfix L00128532. Require same hotfix, for InTouch Japanese xRef SR 48110021 view.exe crash after doing analog input, and then close window. Replicated in IT 10.5 P01. Customer is HIRANO TECSEED CO., Ltd (35305)
Actual Result: | In a window with a historical trend chart, after filling in 3 analog input text boxes, and then pressing a button to close the window. Hd.exe crashes
Expected Result: | These actions should not cause hd.exe to crash

## HFOct48
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5
Component | Redundant DI |  | Ravi Kandula
Hot Fix CR# | L00128752 | Hot Fix Status: | Released-Unverified
Summary: | HF127560 is not addressing the issue of BAD QUALITY status. Need an fix and updated version of HF127560
Actual Result: | 14. Notice that DI Source shows Good Quality and RDI and UDA get stuck with “Bad Quality” status
Expected Result: | UDA should not get stuck with "Bad Quality" status

## HFOct49
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6
Component | App Engine |  | Peter Von tluck
Hot Fix CR# | L00128780 | Hot Fix Status: | Released-Unverified
Summary: | SR45110313: Dillinger Huette "CNmxAdapter::GetAnonymousEngineID - Failed" on a TSE Server. This results in the Clients not receiving any update for values. Request to port fix from L00123729. Customer is unable to apply patch 01.
Actual Result: | The customer was using System Platform 2012 and saw that every 2 to 3 days all of his InTouch applications running through either of his Terminal Servers (CARMIS2 and CARMIS3) would stop displaying live data and display hash (####) instead. A hotfix was created for this. However the customer then upgraded to System Platform 2012 Patch 01. The developers reported that they could not reproduce the issue in Patch 01. Development of the hotfix was stopped. The customer reports that the issue now appears once every 5 weeks. The symptoms are exactly the same. Please visit the Investigation CR L00123389 for more information and for the history of this issue.
Expected Result: | The InTouch applications running through either of the Terminal Servers (CARMIS2 and CARMIS3) shouldn't stop displaying live data.

## HFOct50
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | WW MES 4.0 SP 2
Component | Database Scripts |  | Jim Godfrey
Hot Fix CR# | L00128671 | Hot Fix Status: | Released-Unverified
Summary: | Wonderware North customer JMC steel found issue where the Job events table and job_util_log_Link tables are not correct. The problem seems to be the job_util_log_Link table is not updating the Duration correctly.
Actual Result: | The Job_util_log_link does not should show the correct duration whne compared to the Job event table.
Expected Result: | The Job_util_log_link should show the correct duration whne compared to the Job event table.

## HFOct51
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6
Component | xxSecurity |  | Srinivas Mariyala
Hot Fix CR# | L00128546 | Hot Fix Status: | Released-Unverified
Summary: | SR 15712744 - Poke fails to AppObject attributes, if OSGroup based security configured & integrated with FSGateway. This is for version FSGateway 3.0 with System Platform 2012 R2.
Actual Result: | SR 15712744 - Poke fails to AppObject attributes, if OSGroup based security configured & integrated with FSGateway. This is for version FSGateway 3.0 with System Platform 2012 R2. The issue is with pokes only, reading has no problem. Please investigate this, the end customer is First Solar. The following messages were recorded in the logger - 13891 9/12/2013 9:39:42 AM 16440 3068 Info xxSecurity Security Infraction: User Name: .\user1, User full name: , Node name: SMMES2012P01, Galaxy name: MESIceCreamDemoGalaxy 13892 9/12/2013 9:39:43 AM 6328 13468 Info wwclient DoItemFunction: wwCliAdviseEx() of 'controlsystem.uda1' failed. 13893 9/12/2013 9:41:16 AM 16372 9736 Warning xxSecurity The user ID is {00000000-0000-0000-0000-000000000000}, which is not acceptable for security verification
Expected Result: | Pokes should be successful

## HFOct52
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | InTouch |  | vladimir veselenyi
Hot Fix CR# | L00128748 | Hot Fix Status: | Released-Unverified
Summary: | SR#103129522 PostLogon Dialog box can be hidden behind popups , seems like similar to L00046397, is not reproducible on 3.6 P01
Actual Result: | PostLogon Dialog box can be hidden behind InTouch popup windows what causes application to freeze , seems like similar to L00046397, seems that patch 01 for 3.6 fixed this issue so they want to port the fix to 3.1 SP3 P01
Expected Result: | The dialog box should be modal to all InTouch windows

## HFOct53
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5 Patch01
Component | Engine Category |  | pierluigi iodice
Hot Fix CR# | L00128732 | Hot Fix Status: | Released-Unverified
Summary: | [43810092] - Aguas de Barcelona (S.G.A.B.) - Porting of L00127379 { [SR:45110257: Porsche Stuttgart: Both engines going active at the same time. (This is a quest for an offical release for 2012R2 of the fix in CR L00123982)}
Actual Result: | Customer experienced a problem with both application engines active at the same time in production, causing the system to behave incorrectly. Looking to log files it seems that an engine was started on a server and took over as Active (while nothing is traced by corresponding engine on the other server), but the engine was already active on the other server and both started working in parallel. After engines were redeployed they started working correctly.
Expected Result: | Engines should not get both active at the same time.

## HFOct54
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | LMX |  | Jozef Krehel
Hot Fix CR# | L00128736 | Hot Fix Status: | Released-Unverified
Summary: | SR 42010087 - Thames Water - Errors in SMC :OnNamespaceItemResolved item id returned from service [28612] is different from asked
Actual Result: | The hotfix L00128448 has improved matters - FSGateway no longer hangs when polling for data. However, instead, around 25% of the time the customer gets the following warnings in SMC: OnNamespaceItemResolved item id returned from service [28612] is different from asked for [28611]
Expected Result: | Communication working properly and no warning messages in SMC.

## HFOct55
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | Replication Service |  | Elliott Middleton
Hot Fix CR# | L00128487 | Hot Fix Status: | Released-Unverified
Summary: | Historian Replication does not support the "Wait to send incomplete packets" setting that is exposed for HCAL in the Application Serve Engine settings. This causes increased bandwidth usage in application with lower throughput.
Actual Result: | The AppServer 3.6 Engine configuration includes the option to "Wait to send incomplete packets". There is no corresponding setting for Replication.
Expected Result: | A registry (or similar setting without a UI) to enable the same HCAL setting for Replication. The setting should be applied to all Replication Servers on that "tier 1" Historian.

## HFOct56
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | Extensibility 3.5 Patch01
Component | N/A |  | Manal Hany
Hot Fix CR# | L00128539 | Hot Fix Status: | Released-Unverified
Summary: | SR 48310008: Need HotFix 127907 ported to 3.5P01
Actual Result: | - Customer like to write from a OPCClient Chinese Character to FSGateway and FSGateway to a UDA in the Application Server. Is this possible? Read I could (poke the Chinese character with the ObjectViewer to the uda), InTouch show the character OK. - Could not write and read Chinese Characters through FSGateway to a UDA (String) in the Application Server. Third Party OPC Client --- OPC --- FSGateway --- ArchestrA data source --- WAS V3.6 --- ArchestrA Message Exchange --- InTouch Also, attached word files '' email with details'' contains more details. ---------------------------- could we use the Hotfix 127907 for WAS 3.5 P1 and InTouch V10.5 P1 or do we need a new Hotfix for this version?
Expected Result: | FSgateway should be able to pass Chinese characters (read/write)

## HFOct57
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | AAWebGraphics 5.0
Component | aaWCF Service |  | Alicia Rantos
Hot Fix CR# | L00128730 | Hot Fix Status: | Released-Unverified
Summary: | SR 103129640 - If the InTouch viewer closed, the CPU usage of ArchestrA.Visualizatin.MXPublisherSevice will be high.The service may occupy a whole core of a physical CPU.
Actual Result: | After the InTouch viewer is shutdown, note below issue: 1. CPU usage will up to 80% above, the process occupied CPU is Lmx Publisher Service. 2. After restarting the InTouch viewer, the CPU is still high and doesn't decrease. 3. After restarting the InTouch viewer, the published Window in WIS doesn't work (as if it still cannot connect to InTouch node). The only way to make everything working again is: end the process Lmx Publisher Service in task manager and restart the Service from service panel, or just reboot the WIS node. I have further repeated the same step in InTouch 10.1 and WIS 4.0, the issue didn't exist.
Expected Result: | After the InTouch viewer shutdown, the CPU usage of Lmx Publsher Service should be as normal. After restarting the InTouch viewer, all should back to OK.

## HFOct58
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | Quick Functions |  | Marilou Aguinaldo
Hot Fix CR# | L00128403 | Hot Fix Status: | Released-Verified
Summary: | SR 10417267: View crash due to the Asynchronous function execution while changing Combo Box Values
Actual Result: | The customer is getting assertion errors for deployed InTouchViewApps on random client machines at random times. WindowViewer generally crashes after the errors are acknowledged.
Expected Result: | Investigation for analysis of the crash dumps and corrective measures.

## HFOct59
HotFix Released Detailed
Week: 41, 42, 43, 44 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | View |  | Kevin Nourbakhsh
Hot Fix CR# | L00128710 | Hot Fix Status: | Released-Unverified
Summary: | SR#19818265; Input animation accepts an input with a hover without clicking on it, but inputting without the click view to crash.
Actual Result: | SR#19818265; Input animation accepts an input with a hover without clicking on it, but inputting without the click causes HD to crash. This works fine in IT 10.1 Same Customer also need this hotfix for 10.6 patch01. We are processing the HF request for this issue.
Expected Result: | Shouldn't crash the View