## 工作表1
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.1 SP3 P01
Component | NMXSVC |  | Ali Ibrahim
Hot Fix CR# | L00128562 | Hot Fix Status: | Released-Unverified
Summary: | SR # 44910611: cloned from L00123429 for AppServer 3.1 SP3 P01: If the TSE sessions are closed by windows timeout or by the cross button - an Anonymous Engine is not free released "CNmxAdapter :: GetAnonymousEngineID - FAILED" error appears in logger.
Actual Result: | Customer has 30 Intouch terminal clients. If the sessions are closed by windows timeout or by the cross button - an Anonymous Engine is not free released "CNmxAdapter :: GetAnonymousEngineID - FAILED" error appears in logger. Customer say that when it happens he loses the data coming from the application server. Customer tried to install the HF for CR L00119814 also but it doesn't solve the problem.
Expected Result: | The "Anonymous Engine ID" should be managed correctly also if the sessions are closed by windows timeout or by the cross button.

## 工作表2
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.1 SP3 P01
Component | Engine Category |  | Ali Ibrahim
Hot Fix CR# | L00128628 | Hot Fix Status: | Released-Unverified
Summary: | SR # 41010030: Cloned from HF L00119814: InTouch crashing because Anonymous Engine ID is not recycling correctly. "CNmxAdapter :: GetAnonymousEngineID - FAILED" --- This is a request for porting the fix of HF L00119814 into AppServer 3.1 SP3 P01.
Actual Result: | ** customer available for WebEx session **See log file attached InTouch crashing because Anonymous Engine ID is not recycling correctly. After applying existing workarounds from CRL00082673, tests indicate the issue still exists. Found in 3 of the 6 sites in production each with 4 to 7 clients. The site we have worked on has a TS with 6 clients, after few all values on clients go to NAN. The customer recovers by restarting the TS. From the messages we found the issue was the Anonymous Engine ID not recycling correctly. Customer is using a method to terminate the client sessions which cannot be changed and which does not allow us to use the Log off TSE utility. Based on the following statement from CR L00085908: “… The engine id's aren't recycling if you end the process abnormally (…) If the process is shutdown normally then this wouldn't be a problem” I asked the customer to do everything manually in our final test so we could be sure that even with the workarounds applied, the issue still happened. These were the results: “Here’s the test plan I used: 1) Login to terminal server 2) Start InTouch Viewer 3) Click a few buttons to load various ArchestrA graphics 4) Close the application using ALT-F4 5) Wait 60 seconds (+/- 5 secs) 6) Repeat I did this 10 times, as it has been my experience that the issue is intermittent. I used the registry settings that I had most recently applied. Changing these makes very little difference, in my experience. In this process, two engine IDs were orphaned. The following are the recommendations the customer applied: 1. Enabled Log flags NMXadapter NMXTrace so the messages "NmxAdptr RegisterEngine_ 32767 succeeded" are logged and the engineID monitored. 2. Under "HKLM\Software\Wonderware\InTouch\Installation" the following registry settings must be added LmxMaximumLoopsForShutdown 30 LmxTimeIntervalBetweenLoopsForShutdown 100 The following are other tests results: TEST1 1) RDP’d to the server, started InTouch, closed by using alt-F4, without logging off, started InTouch again (repeated this 7 times) a. The engine ID decreased by 2 2) Remotely controlled a session where InTouch was running, closed InTouch by using alt-F4, which logged out the session (repeated this 7 times) a. The engine ID decreased by 2 I can’t test LogOffTSE, because the customers configuration already logs the user out when view.exe is closed. The registry changes were made just over 2 days ago, and the engine ID is now 32722, meaning that it has decreased by 45. If the rate were constant, we’d see a crash in ~22 days. TEST2 I tried 5 different combinations for the Registry values (some more than once) and saw very little difference in the number of engine IDs orphaned. I n 25 starts of InTouch, there were almost always 4 orphaned IDs +/- 1.
Expected Result: | After applying the recommendations the Anonymous EngineID behavior improved, however there are still orphan IDs. We need to know if this is a is a software defect or WAD. If this few orphan IDs are expected. For the time being, the customer has the following suggestion which will satisfy temporarily, i need an official answer: "Can the current Engine ID be monitored somehow as a failsafe? i.e. can I get to the number that is logged in the SMC when I have the log flag on? If I could get to that value in App Server, I could develop an object which would warn them that they need to schedule a reboot"

## 工作表3
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | Wizards |  | Bindya Shah
Hot Fix CR# | L00128644 | Hot Fix Status: | Released-Unverified
Summary: | SR 12612607: InTouch 2012 R2 RealTimeTrend displays wrong time on time axis
Actual Result: | real time trend stopped showing correct times, it always shows 20:45:52 (or other) wrong time on time axis if Time Span setting is bigger than 14 hours, if the setting is 14 hours then everything is OK, but if setting is > 14 then wrong time is displayed. Other trend settings are: Sample Interval - 2 Min, Time Division Number of Major Div - 5, Time Division Minor Div/Major Div - 1, Bottom Labels
Expected Result: | trend should show always appropriate time

## 工作表4
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | FS Gateway 3.0
Component | Runtime |  | Dan Scott
Hot Fix CR# | L00128439 | Hot Fix Status: | Released-Unverified
Summary: | SR 37113181 - If item activation occurs rapidly, items improperly go to bad quality
Actual Result: | Customer is using FSGateway 3.0 + HF L00127971 (Build 355.226.9.5) Customer is using App Server to FSGateway to Opto OPC Server If non-changing items are rapidly deactivated and reactivated on the Suitelink interface, FSGateway sends only the activate command to the OPC server. Since the OPC server knows that the items are already active, it does not reply with a new OnDataChange update. After nearly 2 minutes, FSGateway logs an error and marks the items as bad quality, since it was waiting for that new data information. The quality will not change until the value changes in the OPC server and a new OnDataChange is received. Error: Initial update from OPC server after activation/creation of item 'Dpoint;State;A_66_15_00_BHCIPRP' in topic 'BH1_DIO' never occurred, injecting bad quality 18h
Expected Result: | FSGateway should properly handle quick deactivation/activation activities

## 工作表5
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5
Component | View |  | Kevin Nourbakhsh
Hot Fix CR# | L00128482 | Hot Fix Status: | Released-Unverified
Summary: | SR#19818246; Input animation accepts an input with a hover without clicking on it, but inputting without the click view to crash.
Actual Result: | SR#19818246; Input animation accepts an input with a hover without clicking on it, but inputting without the click causes HD to crash. This works fine in IT 10.1 Same issue with 10.6, but customer needs the fix for 10.5 no patch We are processing the HF request for this issue.
Expected Result: | Shouldn't crash the View

## 工作表6
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | BatchMngr |  | Matt Mummert
Hot Fix CR# | L00127953 | Hot Fix Status: | Released-Unverified
Summary: | [Genentech] Phase Set Start never happened / Phase stuck in "Writing Parameters"
Actual Result: | Phase received Ready Phase Writing Parameters (nothing further)
Expected Result: | Phase received Ready Phaes Writing Parameters Phase set Start

## 工作表7
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WWInfoServer WIS 5.0 P01
Component | Reporting - Reports |  | piriya karthikeyan
Hot Fix CR# | L00128631 | Hot Fix Status: | Released-Unverified
Summary: | [SR 43610988] Request HF L00127404 for WIS 5.0 P01
Actual Result: | WIS 5.0 P01 is not supported with IE 10
Expected Result: | WIS 5.0 P01 has to be supported with IE 10

## 工作表8
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6
Component | View |  | Tomas Balla
Hot Fix CR# | L00128598 | Hot Fix Status: | Released-Unverified
Summary: | SR# 45110293 - issue: modal dialog causes InTouch hung up under certain conditions
Actual Result: | Invoking a modal Dialog from an InTouch data change script leaves all InTouch controls unresponsive (mouse over / click etc.) unless user clicks back in the original window of the ArchestrA graphics that invoked the data change. If the data change was invoked by an InTouch button, this phenomena does not occur. Test application reproducing this error will follow Refer to investigation CR L00127926 for more details.
Expected Result: | This phenomena not to occur.

## 工作表9
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | History |  | Alex Chia
Hot Fix CR# | L00128532 | Hot Fix Status: | Released-Unverified
Summary: | xRef SR 48110021 view.exe crash after doing analog input, and then close window. Replicated in IT 10.5 P01. Customer is HIRANO TECSEED CO., Ltd (35305)
Actual Result: | In a window with a historical trend chart, after filling in 3 analog input text boxes, and then pressing a button to close the window. Hd.exe crashes
Expected Result: | These actions should not cause view.exe to crash

## 工作表10
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WWInfoServer 5.0
Component | Reporting - Reports |  | Mohamed AbouELSoud
Hot Fix CR# | L00128408 | Hot Fix Status: | Released-Unverified
Summary: | [SR 33913479] Reports called with multiple parameters are returned empty, WIS Report do not hold the selection parameters if there are multiple selection levels.
Actual Result: | "Reports in WIS can be called with parameters. Multiple values, running in Microsoft Reporting Services, in WIS the reports do not work. Page is returned empty." Reporting Server Reports do not hold the selection parameters if there are multiple selection levels and if more than 1 item is selected in the first level. For example, if there are 10 items in the first level, only when one item is selected the second level appears properly. If more than one item or select all is chosen for the first level, then the second level is not active. You will see the report refresh and come back and clear the selection.
Expected Result: | Expect to be able to select more than one item or select all in first level and have the second level active.

## 工作表11
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | AlarmClient (A2) |  | Peter Von tluck
Hot Fix CR# | L00128382 | Hot Fix Status: | Released-Unverified
Summary: | SR 45110228 - If it's used the Alarm Client ".Ack.Selected" method in alarmviewer ocx to acknoledge alarms the Alarm Comment disappear on the EAC .net object.
Actual Result: | Applied Hotfix L00124873. If you acknowlege an archestra alarm by using the alarmviewer.ocx method (or even right mouse click -> ack selected alarm), then the alarm comment in the alarmviewer.ocx stays OK. If you look in paralled to the EAC control, then the alarmcomment has disappeared after the alarm had been acked on the ocx control. If you use EAC only and ack the alarm there it works only with hotfix L00124873 applied.
Expected Result: | EAC should display the alarmcomment even if the alarm had been acknowleded by using the alarmviewer.ocx

## 工作表12
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WW MES 4.5
Component | Client API |  | Jim Eisenhart
Hot Fix CR# | L00128549 | Hot Fix Status: | Released-Unverified
Summary: | Request the 4.5 stateless API DLLs to built to using 'Any platform' in order to execute with 64 Bit Workflow
Actual Result: | Requested by Tom Troy (see Notes for additional information)
Expected Result: | The 4.5 stateless API DLLs (Prod, Util, Quality, etc...) to built to using 'Any platform' in order to execute with 64 Bit Workflow

## 工作表13
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | CEM 1.2
Component | Database Stored Procedures |  | Martin Ouellet
Hot Fix CR# | L00127340 | Hot Fix Status: | Released-Unverified
Summary: | XREF SR#31611965 Subquery returned more than 1 value
Actual Result: | The system stopped storing data and there was a warning message in the log saying: “Subquery returned more than 1 value…” Undeploy and re-deploy of the CEM Engine Service resolved the issue and fortunately all data was recovered in the time that the engine service stopped working.
Expected Result: | No error

## 工作表14
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | CEM 1.5
Component | CEM SummaryDisplay |  | Mohamed Salah
Hot Fix CR# | L00127180 | Hot Fix Status: | Released-Verified
Summary: | SR 103128337 : When I open a WindowViewer page (at the second time) that contain CEMSummaryDisplay symbol the [+] objects near Meters and Events Item have disappeared .
Actual Result: | SR 103128337 : When I open a WindowViewer page (at the second time) that contain CEMSummaryDisplay symbol the [+] objects near Meters and Events Item have disappeared .
Expected Result: | N/A

## 工作表15
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | View |  | Marilou Aguinaldo
Hot Fix CR# | L00128402 | Hot Fix Status: | Released-Verified
Summary: | SR 10417267: Random assertion errors in vumisc.cpp then View crash
Actual Result: | The customer is getting assertion errors for deployed InTouchViewApps on random client machines at random times. WindowViewer generally crashes after the errors are acknowledged.
Expected Result: | view should not crash due to assertion error when using user input animations.

## 工作表16
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | WWPackage Server |  | Marilou Aguinaldo
Hot Fix CR# | L00128462 | Hot Fix Status: | Released-Unverified
Summary: | SR 10417341: Unable to deploy platform to remote client; error "Failed to get the bootstrap's version" [Clone of L00123983; HF for SP2012 R2 P01]
Actual Result: | The customer has gone through the aaBootstrap communications tech note and is able to deploy the GR platform but could not deploy the platform to a remote node. Both the GR and the client are 2008 R2 SP1.
Expected Result: | Requesting that the L00123983 fix be ported for AppServer 3.6 Patch01 as this issue was not listed in the Patch01 Readme under the Resolved Issues and the hotfix resolved the issue for other customers.

## 工作表17
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | Quick Functions |  | Marilou Aguinaldo
Hot Fix CR# | L00128403 | Hot Fix Status: | Released-Unverified
Summary: | SR 10417267: View crash due to the Asynchronous function execution while changing Combo Box Values
Actual Result: | The customer is getting assertion errors for deployed InTouchViewApps on random client machines at random times. WindowViewer generally crashes after the errors are acknowledged.
Expected Result: | Investigation for analysis of the crash dumps and corrective measures.

## 工作表18
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | LicenseInfra 10.1
Component | Managed LCAL |  | Andrea Sartori
Hot Fix CR# | L00128561 | Hot Fix Status: | Released-Unverified
Summary: | SR 43110077: Nestle - When directly access Trend Application by browsing AFweb with Internet Explorer 9 the Trend Control shows Demo Mode.
Actual Result: | When directly access Trend Application by browsing AFweb with Internet Explorer 9 the Trend Control shows Demo Mode. Client side logs shows no response from the License Web Service.
Expected Result: | When License is available, the Trend Client should not go into demo mode.

## 工作表19
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InSQL 11.0
Component | Storage |  | Peter Von tluck
Hot Fix CR# | L00128379 | Hot Fix Status: | Released-Unverified
Summary: | SR45110250: Dillinger-Premium. Trend shows a flat line for MDAS tags after new historyblock had been created.
Actual Result: | Historian version 11: At Dillinger they run a historian with at least 2 GByte data a day. Settings are per default. Tags are retrieved without deadband. IT happens that after historyblock had been created, that the trend shows a flat line for MDAS tags for a certain period. In detail. Imagine 8 h realtime trend. Create a new historyblock at 1 am. Then wait 1 h. Look at the trend: All MDAS tags which are retrieved ( so for the last 8 h means from 6 pm to 2 am show up with a flatline from 1 am to 1.55 am. The last 5 min are well.
Expected Result: | There should be no flatline

## 工作表20
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | Storage |  | Peter Von tluck
Hot Fix CR# | L00128380 | Hot Fix Status: | Released-Unverified
Summary: | SR45110250: Dillinger-Premium. Trend shows a flat line for MDAS tags after new historyblock had been created.
Actual Result: | Historian version 11: At Dillinger they run a historian with at least 2 GByte data a day. Settings are per default. Tags are retrieved without deadband. IT happens that after historyblock had been created, that the trend shows a flat line for MDAS tags for a certain period. In detail. Imagine 8 h realtime trend. Create a new historyblock at 1 am. Then wait 1 h. Look at the trend: All MDAS tags which are retrieved ( so for the last 8 h means from 6 pm to 2 am show up with a flatline from 1 am to 1.55 am. The last 5 min are well.
Expected Result: | There should be no flatline

## 工作表21
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | MxConsumer |  | Jozef Krehel
Hot Fix CR# | L00128448 | Hot Fix Status: | Released-Unverified
Summary: | SR 48810305 - When using FSgateway in a multi-galaxy configuration and adding a large number tags to FSgateway using an OPC Client the tags get stuck in an initializing state. [Porting HF to 3.6 P01]
Actual Result: | When using FSgateway in a multi-galaxy configuration and adding a large number tags to FSgateway using an OPC Client the tags get stuck in an initializing state.
Expected Result: | Able to add a large number of tags in this configuration.

## 工作表22
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | SecMngr |  | Jim Godfrey
Hot Fix CR# | L00128265 | Hot Fix Status: | Released-Unverified
Summary: | Invensys Systems Brazil customer Janssen Cilag has an issue with the Intouch application loses connection to SecMngr.
Actual Result: | They customer is using active X controls with the Security, BatchGuiConfig and OcxBatch controls. They randonly get a disconnect from security manger error and need to restart the Intouch application. This is random and can't be replicated exactly. I get a bact action error 172 when I try.
Expected Result: | The application shuold not disconnet from security Manger.

## 工作表23
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | BatchMngr |  | Matt Mummert
Hot Fix CR# | L00128416 | Hot Fix Status: | Released-Unverified
Summary: | [Genentech] Set Transition on T444 is in infinite retry of tag write
Actual Result: | Tag is being written to, about every 2 seconds for days. Transition is not completing despite the expression assignment having suceeded. Work-Around is to Force the problem Transition and it completes.
Expected Result: | Upon successful assignment (tag write), transition should complete.

## 工作表24
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | SFCOCX |  | Jim Godfrey
Hot Fix CR# | L00128113 | Hot Fix Status: | Released-Verified
Summary: | Bayer - Provide ability to change the colors in the SFC to identify different states
Actual Result: | The customer is looking for a way to change the color in the phase blocks in the SFC when the phase moves from READY to RUN. Currently when the phase transistions to RUN the block is shown in RED for a couple of seconds before it goes Green to indicate RUN state. The customer wants to configure the color between transitions so no RED is shown and the operator is not distracted. Red is a color that implies problems and should not be used in conditions that do not imply problem. Currently the InBatch SFC ActiveX control allows to set different colors to different conditions in the SFC. However this functionality is not working. This functionality seems broken and seems to not allow changing the specific condition described above.
Expected Result: | The customer wants to configure the color shown between transitions so no RED is shown and the operator is not distracted. See below

## 工作表25
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | SFCOCX |  | Jim Godfrey
Hot Fix CR# | L00127976 | Hot Fix Status: | Released-Verified
Summary: | Bayer - Provide ability to change the colors in the SFC to identify different states
Actual Result: | The customer is looking for a way to change the color in the phase blocks in the SFC when the phase moves from READY to RUN. Currently when the phase transistions to RUN the block is shown in RED for a couple of seconds before it goes Green to indicate RUN state. The customer wants to configure the color between transitions so no RED is shown and the operator is not distracted. Red is a color that implies problems and should not be used in conditions that do not imply problem. Currently the InBatch SFC ActiveX control allows to set different colors to different conditions in the SFC. However this functionality is not working. This functionality seems broken and seems to not allow changing the specific condition described above.
Expected Result: | The customer wants to configure the color shown between transitions so no RED is shown and the operator is not distracted. See below

## 工作表26
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5 Patch01
Component | Redundant DI |  | Gary Alldredge
Hot Fix CR# | L00128188 | Hot Fix Status: | Released-Verified
Summary: | SR 10512212 - When redundant application engine fails over, RDI throws unknown errors and becomes quarantined
Actual Result: | ****This is this the same issue as Hotfix L00123603, but I also need the fix for App Server 3.5 P01**** When redundant application engine fails over, RDI throws unknown errors and becomes quarantined. See attached log of example errors.
Expected Result: | App Engine failover with RDi is successful

## 工作表27
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | ABCIP DAServer 4.1 SP3
Component | Runtime |  | Andrea Sartori
Hot Fix CR# | L00128446 | Hot Fix Status: | Released-Unverified
Summary: | [Customer:Nestle][SR:43110340] DAS not communicating properly after renaming a tag on the PLC
Actual Result: | The issue appeared after customer applied some changes to PLC tags that did not propagate properly to the DAS. Starting point is PLC with a tag named MES_PLCCommOK that is written by DAS every second. Topic is configured to auto load/synchronize tags and to use persisted tags (see attached screenshot Config1.png) At this point customer renamed the tag to MES_PLCCommOK_OLD (so that it keeps the same physical address) and created a new tag named MES_PLCCommOK. The DAS did not update properly as it keept writing to the original physical address, that is now used by a different tag (MES_PLCCommOK_OLD ). The behavior did not change resetting the topic nor deactivating/reactivating the DAS, the only way to get it to work was to manually delete the .aaTDB file from the disk. After deactivating/deleting aaTDB/reactivating the DAS is now writing to the correct tag. We performed the same test disabling the "Use Persisted Tags" option (see attached screenshot Config2.png) and keeping the "auto" options; in this case the DAS kept writing to the original address (but wrong tag), manually resetting the topic fixed the issue with DAS now writing to the right location. This time there was no need to manually delete the .aaTDB file, but even if "auto load" and "auto synchronize" options were selected a manual reset of the topic was required.
Expected Result: | DAS should be able to handle the described edits on the PLC.

## 工作表28
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WW MES 4.5
Component | MES Client |  | Oliver Varosanec
Hot Fix CR# | L00128227 | Hot Fix Status: | Released-Unverified
Summary: | Nestle issue -:- SR: 34211454, when creating a Workorder of a process which contains 3 Operations the System does not create a Job for each Operation
Actual Result: | when creating a Workorder of a process which contains 3 Operations the System does not create a Job for each Operation. Lets say you have a Process with 3 Operations and you create a Process Order based on this Process the System will create a Job only for Operation 2 and 3 and not for Operation 1. Analyzing the Issue show that the Problem happened in stored procedure sp_Build_Job_Nonalphabetical (which is called by sp_I_Job_Exec_CWOFP_Stack) This Curser is used to update the Job tables with the Operations. If this system Attribute 340 is not set it will only enter Operations which have a init_prod_pct in the oper_ent_link table of NOT NULL and greater than 0. However when the Operation is created before the Process is saved it worked and init_prod_pcs in oper_ent_link is set to 1. If the Operation is created after the process is saved it will set the init_prod_pcs to NULL and the System will not create a Job for the first Operation of the Process.
Expected Result: | init_prod_pcs in oper_ent_link table should get set properly when a new Operation is assigned to an entity

## 工作表29
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6
Component | InTouch |  | Tomas Balla
Hot Fix CR# | L00128194 | Hot Fix Status: | Released-Unverified
Summary: | SR# 45110293 - issue: modal dialog causes InTouch hung up under certain conditions
Actual Result: | Invoking a modal Dialog from an InTouch data change script leaves all InTouch controls unresponsive (mouse over / click etc.) unless user clicks back in the original window of the ArchestrA graphics that invoked the data change. If the data change was invoked by an InTouch button, this phenomena does not occur. Test application reproducing this error will follow Refer to investigation CR L00127926 for more details.
Expected Result: | This phenomena not to occur.

## 工作表30
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | AlarmClient (A2) |  | Peter Von tluck
Hot Fix CR# | L00128382 | Hot Fix Status: | Released-Unverified
Summary: | SR 45110228 - If it's used the Alarm Client ".Ack.Selected" method in alarmviewer ocx to acknoledge alarms the Alarm Comment disappear on the EAC .net object.
Actual Result: | Applied Hotfix L00124873. If you acknowlege an archestra alarm by using the alarmviewer.ocx method (or even right mouse click -> ack selected alarm), then the alarm comment in the alarmviewer.ocx stays OK. If you look in paralled to the EAC control, then the alarmcomment has disappeared after the alarm had been acked on the ocx control. If you use EAC only and ack the alarm there it works only with hotfix L00124873 applied.
Expected Result: | EAC should display the alarmcomment even if the alarm had been acknowleded by using the alarmviewer.ocx

## 工作表31
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6 Patch01
Component | User Defined |  | Peter Von tluck
Hot Fix CR# | L00128381 | Hot Fix Status: | Released-Unverified
Summary: | Field attribute does not show the correct value unless Buffered Data is selected. This may become a P1 soon
Actual Result: | Field attribute set for integer not historized with a input source going through OPC DI object has the wrong value with good quality He has thousands of points currently in this bad state. They have thousands out FA so setting the buffered data is not a quick fix Seems to work correctly only if we select Buffered data is enabled Seems to happen most with Slow changing FA
Expected Result: | Value should match the PLC

## 工作表32
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | AAWebGraphics 4.0 SP1
Component | aaInTouch Win Converter |  | Mohamed AbouELSoud
Hot Fix CR# | L00128182 | Hot Fix Status: | Released-Verified
Summary: | SR: 45710111 - ArchestrA graphics - missing elements when displayed in WIS
Actual Result: | Customer draws pipes etc with Archestra Graphics. After export to WIS, pipes are missing.
Expected Result: | Full export as the AG looks in Intouch or some error message why elements can't be converted with hints.

## 工作表33
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | Alarm DB Logger |  | Marilou Aguinaldo
Hot Fix CR# | L00128206 | Hot Fix Status: | Released-Unverified
Summary: | SR 10417279: AlarmDBLogger get stuck losing alarms due to an SQL syntax error. Statement terminated string or binary data would be truncated
Actual Result: | See the previous notes. Got a previous hotfix ported but it did not resolve the customer issue.
Expected Result: | If by any reason an SQL statement FAIL the insert in the Alarm DATABASE the alarm db logger should logger an Error in the SMC and remove the alarm from the alarm buffer. Actually when an issue of this type happen the alarm db logger get stuck forever retring the insert causing all buffers to fill up and lose alarm history. This can be a registry option, but for any reason the alarm db logger should stop logging events and alarms. ( in particular if the issue has to do with an "Incorrect syntax .."

## 工作表34
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | ActiveX |  | Peter Von tluck
Hot Fix CR# | L00128383 | Hot Fix Status: | Released-Unverified
Summary: | SR45110233: Dillinger Huette: HistClient ocx is leaking GDI object and private bytes when "use in memory cache" is disabled. It also happens with other ocx (see notes)
Actual Result: | HistClient trend ocx in view.exe leaks GDI objects, handles and private bytes, in case "Use in memory Cache" is disabled. As a result view.exe is running out of resources: Used GDI Handles Count Exceeded the GDI Count Limit for High Priority Windows. I was able to reproduce this in my demo app. Again: Customer is desperatly waiting on the hotfix. Actually he has to restart the view nodes (at least 90<) every second day!!
Expected Result: | there should be no GDI object leak

## 工作表35
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.1 SP3 P01
Component | View |  | Marilou Aguinaldo
Hot Fix CR# | L00128402 | Hot Fix Status: | Released-Unverified
Summary: | SR 10417267: Random assertion errors in vumisc.cpp then View crash
Actual Result: | The customer is getting assertion errors for deployed InTouchViewApps on random client machines at random times. WindowViewer generally crashes after the errors are acknowledged.
Expected Result: | view should not crash due to assertion error when using user input animations.

## 工作表36
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6
Component | Security |  | Tomas Balla
Hot Fix CR# | L00128024 | Hot Fix Status: | Released-Verified
Summary: | SR# 46810184 - When switching Security to Archestra suffix of 5 is attached to all numbers
Actual Result: | Case : Format, under the Regional settings is set to German. When switching Security to ArchestrA a suffix of .5 is attached to all analog tags when shown as textstring. Works as expected when Security is set to "InTouch" and regional settings are english(us).
Expected Result: | No suffix attached.

## 工作表37
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | ArchestrA Graphics |  | Antonio Valieri
Hot Fix CR# | L00128184 | Hot Fix Status: | Released-Verified
Summary: | [XREF SR31310072 - CR L00126056 - Pantek Czech - CEZ a.s.] - Archestra Graphics 'NOT FOUND' red cross in InTouch Viewer after renaming IDE Automation Object.
Actual Result: | After renaming an automation object in IDE, if the object is renamed as another pre-existant object, its graphics in InTouch is marked as 'not found' with the red X even if the graphics is deleted and imported in InTouch Maker.
Expected Result: | After redeploying the intouch app the ArchestrA graphics should be available in InTouch Viewer.

## 工作表38
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5
Component | WWPackage Server |  | Jozef Krehel
Hot Fix CR# | L00127854 | Hot Fix Status: | Released-Unverified
Summary: | SR 103128238 - Objects are checked out after importing localization file
Actual Result: | Customer has template galaxy where after importing localization file alwasy two templates are staying checked out. There are no messages in SMC. In import windows are messages: $MachineTemplate:Object or its descendent(s) is in use. $UnitTemplate:Object or its descendent(s) is in use. In IDE only those two templates are checked out. Validation of whole galaxy logs messages in SMC: Object xxxx is in use. Report Failure. In IDE are than messages $Object_zzzz Good Failed - Object cannot be locked. When I have run galaxy export to aaPkg it always stuck on $CIS_DateTime. After deleting object from galaxy it worked fine but new galaxy created with reimporting of aaPkg shows the same behavior. Creating new galaxy where customer galaxy was used as a template show the same behavior.
Expected Result: | All objects shall be checked in after running import of localization data or shall be some more information in SMC why check-in was not successful. Find root cause of this behavior.

## 工作表39
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6 Patch01
Component | WindowMaker |  | Raghu Kanchanapally
Hot Fix CR# | L00128225 | Hot Fix Status: | Released-Unverified
Summary: | SR 48910064: Window Maker crashed while reshaping the polygon after rubber band zoomin. **Port the HF L00127859 to 10.6 Patch01 version**
Actual Result: | Window Maker crashed while reshaping the polygon after rubber band zoomin. There are 2 scenarios in which it crashes. First while reshaping the polygon by adding a point after rubber band zoom in (this is actual customer's scenario). Second when the window is saved while the polygon is in zoomed in state (this I found while testing). The first scenario is little bit diffcult to reproduce, some times multiple attempts need to be made to see the crash. See the attached WebEx recorder video WM_Crash_1.wrf. (Need WebEx player to play it). The second scenario is consistently reproduced. Every time the window is saved while the polygon is in the zoomed in state, it will crash. See the attached video WM_Crash_2.wrf. I could reproduce both the above crashes on my system. It is more quick to reproduce on customer's system.
Expected Result: | Investigate the crashes and provide a solution so that Window Maker does not crash.

## 工作表40
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5
Component | Keyboards |  | Luca Bruni
Hot Fix CR# | L00126970 | Hot Fix Status: | Released-Unverified
Summary: | SR103127964 The first time you select the "input box" the Windows on screen keyboard doesn't show up and a "u" is show'n in the input box. EnableDisableKeys(1,1,1) in the Startup script. In the viewer configuration check Windows Keyboard.
Actual Result: | Happen in Win Server 2008 32 bit IT 10.5 and W7 32bit IT 10.5. EnableDisableKeys(1,1,1) in the Startup script. In the viewer configuration check Windows Keyboard. Create an input box. The first time you select the "input box" the Windows on screen keyboard doesn't show up and a "u" is show'n in the input box. The solution is restart the view.exe. The second time you open the application it works. Or alternatively enable the WIN button.
Expected Result: | The Windows keyboard should appear.

## 工作表41
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | ActiveFactory 10.1
Component | Trend |  | Brian Nguyen
Hot Fix CR# | L00127207 | Hot Fix Status: | Released-Verified
Summary: | HistClient Desktop Trend gets the following error after opening and closing the AFRWS Trend: "Connection failed - Failed to connect one or more configured servers. Do you want to update the server details?"
Actual Result: | HistClient Desktop Trend gets the following error after opening and closing the AFRWS Trend (on the InfoServer side): "Connection failed - Failed to connect one or more configured servers. Do you want to update the server details?" The user is then required to enter the password for the HisClient Trend login ID that is configured for the Historian data source on the InfoServer side.
Expected Result: | The user shouldn't have to enter the password for the HisClient Trend login ID that is configured for the Historian data source on the InfoServer side. In addition, the desktop trend login shouldn't follow the login configured for the Historian data source on the InfoServer side.

## 工作表42
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | AAWebGraphics 4.0 SP1
Component | aaInTouch Win Converter |  | Mohamed AbouELSoud
Hot Fix CR# | L00128182 | Hot Fix Status: | Released-Unverified
Summary: | SR: 45710111 - ArchestrA graphics - missing elements when displayed in WIS
Actual Result: | Customer draws pipes etc with Archestra Graphics. After export to WIS, pipes are missing.
Expected Result: | Full export as the AG looks in Intouch or some error message why elements can't be converted with hints.

## 工作表43
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | SFCOCX |  | Jim Godfrey
Hot Fix CR# | L00127976 | Hot Fix Status: | Released-Unverified
Summary: | Bayer - Provide ability to change the colors in the SFC to identify different states
Actual Result: | The customer is looking for a way to change the color in the phase blocks in the SFC when the phase moves from READY to RUN. Currently when the phase transistions to RUN the block is shown in RED for a couple of seconds before it goes Green to indicate RUN state. The customer wants to configure the color between transitions so no RED is shown and the operator is not distracted. Red is a color that implies problems and should not be used in conditions that do not imply problem. Currently the InBatch SFC ActiveX control allows to set different colors to different conditions in the SFC. However this functionality is not working. This functionality seems broken and seems to not allow changing the specific condition described above.
Expected Result: | The customer wants to configure the color shown between transitions so no RED is shown and the operator is not distracted. See below

## 工作表44
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.6
Component | SFCOCX |  | Jim Godfrey
Hot Fix CR# | L00128113 | Hot Fix Status: | Released-Unverified
Summary: | Bayer - Provide ability to change the colors in the SFC to identify different states
Actual Result: | The customer is looking for a way to change the color in the phase blocks in the SFC when the phase moves from READY to RUN. Currently when the phase transistions to RUN the block is shown in RED for a couple of seconds before it goes Green to indicate RUN state. The customer wants to configure the color between transitions so no RED is shown and the operator is not distracted. Red is a color that implies problems and should not be used in conditions that do not imply problem. Currently the InBatch SFC ActiveX control allows to set different colors to different conditions in the SFC. However this functionality is not working. This functionality seems broken and seems to not allow changing the specific condition described above.
Expected Result: | The customer wants to configure the color shown between transitions so no RED is shown and the operator is not distracted. See below

## 工作表45
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Extensibility 3.1 SP3 P01
Component | OPC Proxy |  | Ali Ibrahim
Hot Fix CR# | L00128263 | Hot Fix Status: | Released-Unverified
Summary: | SR # 103128784: When the “Block Read” functionality is used on the OPCClient object, the OPCClient itself gets quarantined.
Actual Result: | When the “Block Read” functionality is used on the OPCClient object, the OPCClient itself gets quarantined. The customer uses DASSIDirect 2.0 as the interface between the PLCs and the OPCClient object. He gets the following message in the SMC Logger when the issue happens: OPCClient_S7BlockRead - CBaseRuntimeObject::InternalSetAttribute - Sets are not allowed on a quarantined object. For your information HF L00118505 has been applied, but it didn't help with the issue. The whole SMC Log messages are attached to this CR.
Expected Result: | The "Block Read" functionality should work with no issues and should not cause problems with the "OPCClient" Object.

## 工作表46
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Common 2.0
Component | Admin User |  | Chris Boutcher
Hot Fix CR# | L00126108 | Hot Fix Status: | Released-Verified
Summary: | SR10916638 - : unable to deploy/undeploy or configure objects in AppServer v3.6 with customer GPO enabled; access denied due to insufficient permissions in objects' "...\CheckedIn" and "...\CheckedOut" folders
Actual Result: | <<Log #10916638 - Bret Bolte, Glenmount Global Solutions (on behalf of Beale Air Force Base)>> Customer has restored an AppServer v3.6 galaxy containing WW-Intelligence v1.5 objects from their development offices to the customer's site. Unfortunately, the customer has Global Policy Objects (GPO) that are restricting the ability to deploy/undeploy or configure the Intelligence objects. The aaLogger has messages like: "Error while loading the DataSource Editor: Intelligence.Configuration.Common.IntelligenceException: Error while loading data source '$DataSource_CEMDB'. --> System.UnauthorizedAccessException: Access to the path '\\AMRS-DB01\AMRS-RO\861\CheckedOut\' is denied..." Investigation CR #L00126015 has determined the problem occurs when the computer name is a superset of the domain name. Permissions are not properly propagated to the object's "...\CheckedIn" and "...\CheckedOut" folders for the user logged into IDE.
Expected Result: | Paul Forney suspects it may be an issue with the C++ interface may be returning the wrong data (the COM interface used to set the RunAs permissions seems to work correctly). Permissions need to be properly propagated to the necessary folders when the computer name is a superset of the domain name.

## 工作表47
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | FS Gateway 3.0
Component | Runtime |  | Dan Scott
Hot Fix CR# | L00127971 | Hot Fix Status: | Released-Verified
Summary: | SR 37113120 - FSGateway does not correctly handle OPC AddItem error per OPC Specifications. In this case, it causes stale data with good quality.
Actual Result: | Please see the attached HF Details document. It contains extensive details about the problems encountered, OPC trace examples, and OPC Specification references, and expected behaviors. I used Word's commenting feature to callout key points. If you cannot see these comment ballons, please let me know. To summarize the issue: When FSGateway requests an OPC item that is invalid, it incorrectly registers the client handle of the invalid item, even though the OPC server reported the item as invalid. Per OPC specifications, the invalid item should be ignored (OPCClient object does this correctly). Then when the item is removed from FSGateway, it incorrectly tries to unsubscribe the item from the OPC server, even though the OPC server refused the initial subscription. This results in either a simple error within the OPC server that the item is not on the subscription list, or it results in the wrong item being removed if the handle was reused (which is allowed per spec - see below.) In the customer's situation, valid items start registering with client handle 0x00000000. When an invalid item is requested, it reports as 0x00000000 as well, since there is no handle. Then when the invalid item request is removed from FSGateway, it unsubscribes 0x00000000 (the new invalid item). This leaves the old valid item 0x00000000 in the diagnostic view with good quality, but it stops getting updates since we've now told the OPC server to stop sending us that item. The result is stale data in the customer application. In this case the ppError code on the AddItem attempt is 'OPC_E_INVALIDITEMID'; however, this fix should accomidate all error responses. This error is exposed because the OPC Server vendor starts server handles at 0x00000000. I am also going to request that they change this behavior to start at some number other than 0.
Expected Result: | FSGateway should ignore server handles for items that are reported as errors during the AddItem call. Account for the fact that the server handle may already exist for some other valid item. These items should not be on the active subsciption list when RemoveItems is called.

## 工作表48
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Extensibility 3.6
Component | N/A |  | Manal Hany
Hot Fix CR# | L00127907 | Hot Fix Status: | Released-Verified
Summary: | SR 14413640: could I write with a OPC Client Chinese character to a AA UDA String?
Actual Result: | - Customer like to write from a OPCClient Chinese Character to FSGateway and FSGateway to a UDA in the Application Server. Is this possible? Read I could (poke the Chinese character with the ObjectViewer to the uda), InTouch show the character OK. - Could not write and read Chinese Characters through FSGateway to a UDA (String) in the Application Server. Third Party OPC Client --- OPC --- FSGateway --- ArchestrA data source --- WAS V3.6 --- ArchestrA Message Exchange --- InTouch Also, attached word files '' email with details'' contains more details.
Expected Result: | FSgateway should be able to pass Chinese characters (read/write)

## 工作表49
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Bogus CRs Only test1
Component | Bogus component |  | Daniela Tulbure
Hot Fix CR# | L00099962 | Hot Fix Status: | Released-Unverified
Summary: | test- disregard
Actual Result: | a
Expected Result: | a

## 工作表50
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WWInfoServer 5.0
Component | Reporting Web Site (RWS) |  | Keynon Basinger
Hot Fix CR# | L00127873 | Hot Fix Status: | Released-Unverified
Summary: | SR 103128389- Historian Cleint Reports using Bound Times do not publish with correct times.
Actual Result: | SR 103128389- Historian Cleint Reports using Bound Times do not publish with correct times.
Expected Result: | Should allow customer to generate report with custom time range.

## 工作表51
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WWInfoServer 5.0
Component | Query |  | piriya karthikeyan
Hot Fix CR# | L00127740 | Hot Fix Status: | Released-Unverified
Summary: | [SR 35312334] running query with multiple Historians does not save the historians
Actual Result: | running query with multiple Historians does not save the historians. Info Server does not keep all the added Historians once the browser is closed and reopened.
Expected Result: | The added historians should be saved and when reopend, it should be there.

## 工作表52
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | ActiveFactory 10.0 SP2
Component | Trend |  | Alex Chia
Hot Fix CR# | L00126382 | Hot Fix Status: | Released-Unverified
Summary: | SR 46110132 - The application crashes on site every 2-3 days. Replicated issue in lab, by opening and closing multiple different pop-up with Hist Client Trend. Memory leak does not seem to be a cause as it does not rise significantly
Actual Result: | As the different "Detail" buttons are pressed in "CUB-Graphic [UT]SingleLine#X" window, to display the pop-up window with the Historian Client Trend Active X control and other animation links, after a certain number of the display's are shown, one after another, the application will crash. The InTouch application is randomly crashing on site during commisioning causing delays in completing the project. Customer re-evaluating software for upcoming new project.
Expected Result: | Windowviewer continue to run without crashing, even though pop-ups are periodically open and closed.

## 工作表53
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.6
Component | Security |  | Tomas Balla
Hot Fix CR# | L00128024 | Hot Fix Status: | Released-Unverified
Summary: | SR# 46810184 - When switching Security to Archestra suffix of 5 is attached to all numbers
Actual Result: | Case : Format, under the Regional settings is set to German. When switching Security to ArchestrA a suffix of .5 is attached to all analog tags when shown as textstring. Works as expected when Security is set to "InTouch" and regional settings are english(us).
Expected Result: | No suffix attached.

## 工作表54
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InSQL 11.0 Patch 01
Component | OLE-DB Provider |  | Brian Nguyen
Hot Fix CR# | L00128171 | Hot Fix Status: | Released-Unverified
Summary: | SR41111042, SR14812363 - ERROR: GetNextDataQueryResult failed (4;2013/04/09: 10:44:13.665 --> 11:44:13.665; 8996; bl_packer1_Dat_badge; error = 7 (Cache overflow)) [AMFG4; o_pdsqry.cpp; 281]
Actual Result: | Customer upgraded Historian from version 10.0 SP1 P01 to 11.0. The system has multiple instances of a 3rd party application hitting the Historian Server to retrieve data values from the server. After about an hour or so, the ArchetrA logger on the Historian Server is filled up with the following message, and the ahRetSvc.exe is using very high CPU (about 70 - 76 % CPU usage.) ERROR aahCfgSvc GetNextDataQueryResult failed (4;2013/04/09: 10:44:13.665 --> 11:44:13.665; 8996; bl_packer1_Dat_badge; error = 7 (Cache overflow)) [AMFG4; o_pdsqry.cpp; 281] This problem is causing big problem on the production system and needs to be resolved quickly.
Expected Result: | Problem should not happen. It used to work for older Historian v10.0 SP1P01.

## 工作表55
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.5 Patch01
Component | Redundant DI |  | Gary Alldredge
Hot Fix CR# | L00128188 | Hot Fix Status: | Released-Unverified
Summary: | SR 10512212 - When redundant application engine fails over, RDI throws unknown errors and becomes quarantined
Actual Result: | ****This is this the same issue as Hotfix L00123603, but I also need the fix for App Server 3.5 P01**** When redundant application engine fails over, RDI throws unknown errors and becomes quarantined. See attached log of example errors.
Expected Result: | App Engine failover with RDi is successful

## 工作表56
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | FS Gateway 3.0
Component | Runtime |  | Peter Von tluck
Hot Fix CR# | L00125820 | Hot Fix Status: | Released-Unverified
Summary: | SR14413602: Philip Morris: FSGateway: $sys$pollnow is not implemented in FSGateway. OPCLink has pollnow instead.
Actual Result: | in OPCLink the system item "pollnow" allowed to get all items refreshed by message arbitration. This is not possible with FSGateway: pollnow or $sys$pollnow is not implemented. Customer uses a workaround instead: $sys$reconnect: This is not the same and creates a lot of problems!!
Expected Result: | $sys$pollnow should be implemented in FSGateway

## 工作表57
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | Industrial Application Server 3.6
Component | Redundant DI |  | Rich Liddell
Hot Fix CR# | L00128094 | Hot Fix Status: | Released-Unverified
Summary: | Customer Nestle: If the instances have bad items that do not exist in the PLC the RDI seems to take the engine down. The CPU increases for the engine and the time idle average decreases to zero and the engine stops responding over night.
Actual Result: | If the instances have bad items that do not exist in the PLC the RDI seems to take the engine down. The CPU increases for the engine and the time idle average decreases to zero and the engine stops responding. if the RDI is redeployed the engine will go back to normal and start degrading again over night
Expected Result: | Bad items should not cause the RDI to take the engine down

## 工作表58
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | ArchestrA Graphics |  | Antonio Valieri
Hot Fix CR# | L00128184 | Hot Fix Status: | Released-Unverified
Summary: | [XREF SR31310072 - CR L00126056 - Pantek Czech - CEZ a.s.] - Archestra Graphics 'NOT FOUND' red cross in InTouch Viewer after renaming IDE Automation Object.
Actual Result: | After renaming an automation object in IDE, if the object is renamed as another pre-existant object, its graphics in InTouch is marked as 'not found' with the red X even if the graphics is deleted and imported in InTouch Maker.
Expected Result: | After redeploying the intouch app the ArchestrA graphics should be available in InTouch Viewer.

## 工作表59
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | WindowMaker |  | Raghu Kanchanapally
Hot Fix CR# | L00127859 | Hot Fix Status: | Released-Verified
Summary: | SR 48910046: Window Maker crashed while reshaping the polygon after rubber band zoomin.
Actual Result: | Window Maker crashed while reshaping the polygon after rubber band zoomin. There are 2 scenarios in which it crashes. First while reshaping the polygon by adding a point after rubber band zoom in (this is actual customer's scenario). Second when the window is saved while the polygon is in zoomed in state (this I found while testing). The first scenario is little bit diffcult to reproduce, some times multiple attempts need to be made to see the crash. See the attached WebEx recorder video WM_Crash_1.wrf. (Need WebEx player to play it). The second scenario is consistently reproduced. Every time the window is saved while the polygon is in the zoomed in state, it will crash. See the attached video WM_Crash_2.wrf. I could reproduce both the above crashes on my system. It is more quick to reproduce on customer's system.
Expected Result: | Investigate the crashes and provide a solution so that Window Maker does not crash.

## 工作表60
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | WWInfoServer 4.0 SP1
Component | Graphics |  | Mohamed Salah
Hot Fix CR# | L00127818 | Hot Fix Status: | Released-Unverified
Summary: | SR 40214964 : Suite Voyager Information Server - two graphic pages work in IE6 but not IE8 IE9
Actual Result: | Suite Voyager Information Server - two graphic pages work in IE6 but not IE8 IE9 on Windows 7 Client PC
Expected Result: | Suite Voyager Information Server - two graphic pages should work in IE6 ,IE8 and IE9

## 工作表61
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | Alarm DB Logger |  | Tomas Balla
Hot Fix CR# | L00127949 | Hot Fix Status: | Released-Unverified
Summary: | SR# 103129226 - Requesting the French version of L00126142 - The statement has been terminated. String or binary data would be truncated
Actual Result: | Customer has the same issue as in L00126142. They need the french verison of L00126142. Our Customer ADP (CF ID 108750) have been stuck during alarm storage. He have a huge quantity of messages in his logs like : "The statement has been terminated. String or binary data would be truncated"
Expected Result: | French version of L00126142

## 工作表62
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | MBTCP DAServer 3.0 SP1
Component | Runtime |  | Dan Scott
Hot Fix CR# | L00127764 | Hot Fix Status: | Released-Verified
Summary: | SR 103128993 - DASMBTCP process terminates crashes and restarts constantly
Actual Result: | Customer is using App Server 3.6 OPCClient objects to read from DASMBTCP. When everything is deployed, the DASMBTCP process crashes and restarts constantly.
Expected Result: | No DASMBTCP crashes

## 工作表63
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InBatch InBatch 9.5 SP1
Component | BatchMngr |  | Jim Godfrey
Hot Fix CR# | L00127889 | Hot Fix Status: | Released-Verified
Summary: | InBatch Manual Equipment Selection List behavior of Units added and removed incorrectly, for example after changes to unit status.
Actual Result: | As reported from Genentech interfaces testing, Batch Display Equipment Selection displays equipment (units) and their statuses that can be acquired. If one changes a unit to a different status that is not in the profile or is not defined, the equipment disappears from the display as designed. If one then enters another status not in the profile or not defined, the unit appears in the Equipment Selection display no matter the status. Another change of status not in the profile will cause to the unit to disappear and it will re-appear on the next status change. If one selects the unit with a status not in the profile and pushes the "Allocate" button, then unit will NOT be Allocated.
Expected Result: | Equipment with unavailable status should not be in Manual Equipment Selection list. Equipment with available status should be in Manual Equipment Selection list.

## 工作表64
HotFix Released Detailed
Week: 36, 37, 38, 39, 40 - 2013
ArchestrA Reports
Product | InTouch 10.5 Patch01
Component | WindowViewer |  | Tomas Balla
Hot Fix CR# | L00127893 | Hot Fix Status: | Released-Verified
Summary: | [XREF SR103128950 - Pantek Czech] - Interactive animation link doesn't work with 'Halo follow object shape' on InTouch line drawn under angle 315? (3/2 pi rad)
Actual Result: | If in Window Maker a line is drawn with an angle of 315° and animated, after changing Window Viewer behavior to 'Halo Follow Object shape', the animation doesn't work and the halo is not drawn. Asked customer to avoid to use the 'Halo follow object shape option' as workaround. Workaround is not acceptable as the InTouch app is a railway application and the customer needs to click on tracks and be sure on which object they are clicking on.
Expected Result: | Halo and animation must work also with lines drawn at 315° angle (and more).